## Slide 1
Bioenergy Research and Demonstration Facility
MARCH 2015 - UPDATE

## Slide 2
By constructing this facility on the UBC campus, lessons can be learned and shared with other universities, communities, governments, and industry that will result in the advancement of new ideas that will meet operational needs, generate new research, and contribute towards the global challenges of climate change
Key operational questions addressed by the BRDF:
Can wood waste destined for the landfill be used to generate thermal energy and/or electricity?
Is biomass a viable method for greenhouse gas emissions reductions?
Is cogeneration from biomass syngas commercially viable?
Can common community concerns with respect to emissions and vehicle traffic from biomass operations be addressed?
Can the benefits of localized (distributed) power generation be monetized?
Can cross-laminated timber (CLT) construction be an added-value industry in British Columbia?
What was the BRDF all about?

## Slide 3: Who’s Involved
UBC Operations, Faculty, Students, Researchers; with industry partners: Nexterra, General Electric, BCHydro; and the local community: UNA, SHHS
UBC project partners include:
  BC Bioenergy Network
  BC Ministry of Energy, Mines
  BC Ministry of Forests
  BC Hydro
  Ethanol BC
  City of Vancouver
  FP Innovations
  GE Energy
  Natural Resources Canada
  Nexterra Systems Corp.
  Sustainable Development Technology Canada

## Slide 4: What is the BRDF?
Summary
Biomass cogeneration demonstration project using syngas clean up technology A social license demonstration A $27.4M multi-partnership project Building constructed from Canadian produced Cross Laminated Timber (CLT) Thermal Mode: 6 MWt or Cogeneration Mode: 2.9 MWt & 2MWe
Why the BRDF made sense?
Positive return on UBC’s investment within 15 years. 12% reduction of UBC CO2 emissions and offsetting the consumption of 150,000 GJ of natural gas at the Powerhouse Diversifies UBC’s thermal fuel source mix. “Campus as a Living Lab” collaboration between Faculty, Operations & Industry
Notes: Thermal Mode: 20,000 lb/r
Cogen Mode: 9600 lb/hr

## Slide 5
Modes of operation: Thermal only or Research Cogeneration Mode
Biomass Gasifier
Equipment
Installed
Production
Steam Boiler
Steam
6 MWt peak in Thermal Mode
Engine & HRSG
2 MWe Electrical
1.4 MWt Steam
1 MWt Hot Water
1.5 MWt in CHP mode
Thermal Only
Biomass Cogeneration
Notes: Commercial (Thermal)
  → produces 20k lbs/hr steam ( 25% of current campus use)
Demonstration (Thermal & Electricity)
  → produces 1.9 MWe (gross) electrical power ( 5% of Campus demand) and 9.6k lbs/hr steam ( 12% of current campus use)
Goal:
Demonstrate technical and commercial viability of 2 MWe combined heat and electrical power bioenergy system

## Slide 6
What were the social licence barriers of the BRDF?
biomass sourcing
building siting
truck traffic
air emissions
What were some of the barriers overcome / lessons learned?

## Slide 7: Fuel (Biomass) Sourcing
Fuel is ground & chipped waste wood:
  Sawmill residuals
  Furniture/carpentry offcuts
  Municipal trimmings
  Land clearing operations
Fuel is renewable as it diverts wood waste from landfills where it would otherwise rot and produce methane.
Uses 2-4 trucks per day for 12,500 dry tonnes per year.
Notes: Operational ~100 days

## Slide 8: Social License: BRDF Siting
The site was chosen to be a first of its kind in BC, for a social license, to demonstrate a biomass/cogeneration facility in a high density urban setting
Secondary consideration for site was the close proximity to Marine Drive and operational support
Childcare
Housing
Housing
Childcare

## Slide 9: Above & beyond: Ambient Air Monitor
Emission Dispersion Study showed Marine Tower 5 as the most likely residential building for air emission impact
June 2012, UBC proactively installed a real time Ambient Air Monitor on Marine Tower 5
Automatic emails alerts if air quality limits are exceeded
  24 hour average PM 2.5 < 25 µg/m3 or
  1 hour NO2 < 107 ppb
Air emissions remain well below Metro Vancouver limits
Notes: Emission Dispersion Study identified the top of Marine Tower #5 to be the worse case scenario for air containments from the BRDF
June 1st 2012 RWDI completed the installation of the ambient air monitor on the roof of the adjacent student residences building.
Monitor provides real time data for ambient levels of:
  PM 2.5
  NO2
  NO
Automatic emails are sent to BO if levels exceed the Metro Vancouver air quality objectives of
  24 hour average PM 2.5 < 25 µg/m3
  1 hour NO2 < 107 ppb

## Slide 10: BRDF Air Emissions (Performance)
Verified by 3rd party testing (Al Franco)
Unless otherwise noted, all units are in mg/m3
Boiler | 
Permit | Test
15 | 2.1
272 | 230
10.5 | 2.2
5% | 0%
Engine | 
Permit | Test
15 | 1.3
249.7 | 105
40.9 | 31
5% | <5%
Permit Requirements
PM Particulate Matter
NOx Nitrogen Oxides
VOC Volatile Organic Compounds
Opacity
Dryer | 
Permit | Test
15 | 3.9
- | -
10.4 | 9.6
5% | <5%

## Slide 11
How are we using the BRDF to advance research/industry?
Photo Credit: Don Erhardt
Notes: Operational ~100 days

## Slide 12
The active commercial operation of the UBC system spawned the development of 11 spin‐off R&D projects at UBC engaging 14 UBC faculty and a larger number of students
Catalytic Tar Cracking - Primary Investigator: Dr. John R Grace, Dr. Tony Bi
High Temp. Hydrogen Membrane Extraction - Primary Investigator: Dr. John R Grace, Dr. Jim Lim
CLT Life Cycle Study - Primary Investigator: Dr. Alberto Cayuela
MetroVancouver Fuel Study - Primary Investigator: Dr. Shahab Sokhansanj, Dr. Anthony Lau
Implication on testing of pipeline materials exposed to hydrogen - Primary Investigator: Dr. Chad Sinclair, Dr. Matt Roy
Added Value Ash Study - Primary Investigator: Dr. Tom Troczynski
Examination of Corrosion Mechanisms in Steel Vessels - Primary Investigator: Dr. Akram Alfantazi
Metallurgical Investigation of Materials Issues at the BRDF - Primary Investigator: Dr. Steve. Cockcroft
B2H Advanced Gas Program - Primary Investigator: Nexterra/UBC/Fortis/Quadrogen
Electro‐Chemical Energy Storage (ECES) - Primary Investigator: Dr. Martin Ordonez
Advanced Integrated AC‐DC Systems - Primary Investigator: Dr. Juri Jatskevich
BRDF: RESEARCH ACTIVITIES
Photo Credit: Don Erhardt
Notes: Operational ~100 days

## Slide 13
  ### of Tours
  International/High profile Visitors
  Awards
How has this project enhanced UBC’s reputation?

## Slide 14
  ### of Tours
  International/High profile Visitors
  Awards
Building UBC’s reputation
400+ Tours:
Creative Energy, University of Hokkaido, Office of Energy Research and Development, Sustainable Development Canada, University of Antwerp, UBS Global Asset Management, FortisBC, SFU, and others
Awards:
  2012 LEED Gold Building
  2012 KPMG Infrastructure 100 Award: Outstanding efforts in urban infrastructure
  2013 Canadian Wood Council Wood Building & Design Award: In recognition of excellence in architectural design using wood for commercial large projects.

## Slide 15
Reference site for Nexterra’s United Kingdom contracts (first of five)
Metro Vancouver: Biomass Social License
Successful technology development option for both the federal and provincial government
FortisBC – Renewable Natural Gas (RNG)
GE first dual fuelled gas engine
Commercial Applications of Cross Laminated Timber
Building UBC’s reputation

## Slide 16
2 MVA contribution to electrical capacity constraint issue.
Mitigated peak capacity of powerhouse boilers (originally approved to be replaced in 2008/09)
Etc…
How has the BRDF performed?

## Slide 17
Spring 2009 BRDF Concept devised
Spring- Fall 2010 Public Engagement
April 2010 UBC Board Approval
Feb. 2011 Groundbreaking
July 2012 Thermal Mode Commissioned
Sept 2012 Grand Opening Ceremony
Oct. 2012 Combined Heat + Power (CHP) Mode Commissioned
Nov. 2012 Full Operation
July 2014 Renewable Natural Gas (RNG) CHP Commissioned
Project Roadmap
Construction May 2011
Construction Jan 2012
Construction May 2012

## Slide 18: PERFORMANCE: LESSONS LEARNED (Biomass Cogeneration)
Syngas clean up process equipment failures. Requires several system upgrades to resolve
Requires a higher biomass fuel quality than expected (<30% moisture content)
Higher operational costs than expected e.g. people, maintenance and materials
Notes: Higher Operational Costs
  No additional labour was accounted for Cogen Operations. It is a 5 day process with 2 man 24/7 operators to get the engine running.
  Carbon annual costs of 365k vs 150k in OBC
Higher fuel quality is required
  <30% Moisture for CHP startup until engine is running and dryer is available

## Slide 19: PERFORMANCE: ENHANCED
BRDF | Biomass Thermal | Biomass Cogeneration
Steam Boiler | 6.0 MWt (20,000lbs) | 1.5 MWt (5,000lbs)
Heat Recovery Steam Generator (HRSG) | - | 1.4 MWt (4,600lbs)
Hot Water Engine Heat Recovery | - | 1 MWt
Electrical Energy | - | 2 MWe
TOTAL | 6 MW | 5.9 MW
Biomass Thermal & RNG Cogeneration
6.0 MWt (20,000lbs)
1.4 MWt (4,600lbs)
1 MWt
2 MWe
10.4 MW*
Note 1MWt = 1 MegaWatt (thermal) = 3,333lbs steam
*75% increase in energy production

## Slide 20
BRDF Project | Original Business Case | The Current Situation
Remaining principle ($8.35M loan) | $8.35M | $7.4M
Annual O&M cost | $1.4M | $1.1M
Annual fuel input cost1 | $0.8M | $2.6M
Price of Natural Gas (2015) | $11.1/GJ | $8.5/GJ
Revenue generated | $3.2M | $3.9M
break-even forecast2 | 2026 | 2028
Fuel Input costs are considerably higher due to 1) the use of renewable natural gas as the primary fuel for cogen, and 2) the plant is now operating in full thermal and cogen modes simultaneously. The break-even forecast is extended by 2 years due to 1) the delayed completion of the project, and 2) our unsuccessful efforts to reliably produce electricity from syngas. |  | 
Photo Credit: Don Erhardt
 | FY15
Steam Produced (MWh) | 40,000
Portion of Campus Thermal load from the BRDF | 23.4%
GJ of natural gas offset | 145,000 GJ
Tonnes CO2 offset | 6,780
Electricity Produced (MWh) | 9,900
BRDF PERFORMANCE
Notes: Operational ~100 days
Steam Produced (Million of lbs): 110.7 Thermal mode + 22.3 HRSG steam + 7.2 Hot water = 140.2 million of lbs
Portion of Campus Use(Million of lbs): Total production = 645.0, total campus use = 612.6
GJ of NG offset = 145,999GJ from thermal mode + 29,425 GJ HRSG + 9,439 GJ HW = 184,863 GJ
Thermal mode Tonnes CO2 offset = thermal mode Gas offset = 7298 tCo2, thermal mode gas addition: -72tCo2, biomass carbon add: -345tCo2 = 6880 tCo2
Electricity Produced (Mwh) 9806 MWh

## Slide 21
2 MVA contribution to electrical capacity constraint issue.
Mitigated peak capacity of powerhouse boilers (originally approved to be replaced in 2008/09)
Etc…
BRDF PERFORMANCE
Mitigates UBCV electricity capacity constraints
Mitigated steam capacity constraint and avoided powerhouse boiler replacement cost.
Enables transition from the existing powerhouse to the new campus energy centre by providing the thermal summer base load of the campus (2015).

## Slide 22: NEXT STEPS:
Continue to work with FortisBC to reduce the cost of renewable natural gas.
Continuous improvement to operations and efficiency.
Pre-feasibility study of expanded biomass operation to meet 2020 greenhouse gas reduction target.

## Slide 23: Thank You
David Woodson
Managing Director, Energy + Water Services
david.woodson@ubc.ca